{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":15,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-CFXR"]
[]
[]
[]
[]
["","","","","EWAD600CFXR","EWAD740CFXR","EWAD820CFXR","EWAD870CFXR","EWAD980CFXR","EWADC10CFXR","EWADC11CFXR","EWADC12CFXR","EWADC13CFXR","EWADC14CFXR","EWADC15CFXR"]
["Sound pressure level","Cooling","Nom.","dBA","71 (3)","72 (3)","72 (3)","72 (3)","72 (3)","73 (3)","72 (3)","72 (3)","72 (3)","73 (3)","73 (3)"]
["Refrigerant charge","Per circuit","","kg","64.0","73.0","81.0","81.0","91.0","91.0","107.0","107.0","112.5","124.0","124.0"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","TCO2Eq","91.5","104.4","115.8","115.8","130.1","130.1","153.0","153.0","160.9","177.3","177.3"]
["Compressor","Type","","","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw","Asymm single screw"]
["","Quantity","","","2","2","2","2","2","2","2","2","2","2","2"]
["Weight","Operation weight","","kg","8,795","9,390","9,995","9,995","11,459","11,719","13,566","13,566","14,806","14,886","14,936"]
["","Unit","","kg","8,050","8,620","9,190","9,190","10,450","10,710","12,190","12,190","12,830","12,910","12,960"]
["Air heat exchanger","Type","","","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type"]
["EER","","","","2.29 (1), 12.91 (2)","2.66 (1), 13.17 (2)","2.75 (1), 14.04 (2)","2.59 (1), 13.71 (2)","2.67 (1), 14.33 (2)","2.51 (1), 13.89 (2)","3.05 (1), 15.36 (2)","2.90 (1), 14.87 (2)","2.95 (1), 14.7 (2)","2.79 (1), 13.85 (2)","2.66 (1), 13.56 (2)"]
["ESEER","","","","3.59","3.66","3.89","3.62","3.83","3.63","4.13","3.89","4.09","4.02","3.92"]
["Refrigerant","GWP","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Type","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Circuits","Quantity","","2","2","2","2","2","2","2","2","2","2","2"]
["Cooling capacity","Nom.","","kW","602 (1), 374 (2)","739 (1), 468 (2)","821 (1), 539 (2)","866 (1), 562 (2)","981 (1), 644 (2)","1,034 (1), 670 (2)","1,229 (1), 825 (2)","1,302 (1), 866 (2)","1,374 (1), 889 (2)","1,424 (1), 909 (2)","1,476 (1), 929 (2)"]
["Water heat exchanger","Water volume","","l","741","771","808","808","1,012","1,012","1,372","1,372","1,965","1,965","1,965"]
["","Type","","","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube"]
["Power input","Cooling","Nom.","kW","263 (1), 46.6 (2)","278 (1), 56.2 (2)","299 (1), 58.5 (2)","334 (1), 63.1 (2)","368 (1), 68.5 (2)","412 (1), 74.4 (2)","403 (1), 80.0 (2)","450 (1), 87.5 (2)","466 (1), 93.4 (2)","511 (1), 103 (2)","556 (1), 109 (2)"]
["Sound power level","Cooling","Nom.","dBA","92","92","92","92","94","94","94","95","95","95","95"]
["Dimensions","Unit","Width","mm","2,480","2,480","2,480","2,480","2,480","2,480","2,480","2,480","2,480","2,480","2,480"]
["","","Depth","mm","6,300","7,200","8,100","8,100","9,000","9,000","10,800","10,800","10,800","10,800","10,800"]
["","","Height","mm","2,565","2,565","2,565","2,565","2,565","2,565","2,565","2,565","2,565","2,565","2,565"]
["Capacity control","Minimum capacity","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["","Method","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Fan","Air flow rate","Nom.","l/s","38,935","46,722","54,508","54,508","62,295","62,295","73,011","73,011","73,011","73,011","73,011"]
["","Speed","","rpm","715","715","715","715","715","715","715","715","715","715","715"]
["Compressor","Starting method","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 16°C; leaving evaporator water temp. 10°C; ambient air temp. 35°C; full load operation."]
["","","","","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C.","(2) - Data is calculated at ambient air temperature 5°C, inlet water temperature 16°C."]
["","","","","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744","(3) - Cooling: evaporator 16/10°C, ambient 35°C, unit at full load operation; standard: ISO 3744"]
["","","","","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(5) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %"]
["","","","","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(6) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(7) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(9) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(11) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding"]
["","","","","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(12) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1"]
["","","","","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)","(13) - Unit performances refer to ideal running conditions that are reproducible in laboratory test environment in accordance to recognized industry standards (i.e. EN14511)"]
["","","","","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory","(14) - Weight and dimensions are indicative, for specific values refer to certified drawings issued by the factory"]
["","","","","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book","(15) - For specific information about additional options refer to the options section in the data book"]