{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":47,"n_cols":12,"rows_kept":47,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYQ-CWN"]
[]
[]
[]
[]
["","","","","","EWYQ016CAWN","EWYQ021CAWN","EWYQ025CAWN","EWYQ032CAWN","EWYQ040CAWN","EWYQ050CAWN","EWYQ064CAWN"]
["Cooling capacity","Nom.","","","kW","16.8 (1)","21.0 (1)","25.3 (1)","31.6 (1)","42.1 (1)","50.5 (1)","63.2 (1)"]
["Capacity control","Method","","","","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled"]
["","Minimum capacity","","","%","25","25","25","25","25","25","25"]
["Power input","Cooling","","Nom.","kW","5.93 (1)","7.61 (1)","9.60 (1)","12.9 (1)","15.1 (1)","19.2 (1)","25.7 (1)"]
["EER","","","","","2.84","2.77","2.63","2.45","2.79","2.63","2.46"]
["Dimensions","Unit","","Depth","mm","774","774","774","774","780","780","780"]
["","","","Height","mm","1,684","1,684","1,684","1,684","1,684","1,684","1,684"]
["","","","Width","mm","1,370","1,370","1,370","1,680","2,360","2,360","2,980"]
["Weight","Unit","","","kg","268","321","321","403","579","579","741"]
["Casing","Colour","","","","Daikin White","Daikin White","Daikin White","Daikin White","Daikin White","Daikin White","Daikin White"]
["","Material","","","","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate","Polyester coated galvanised steel plate"]
["Air heat exchanger","Type","","","","Air cooled coil","Air cooled coil","Air cooled coil","Air cooled coil","Air cooled coil","Air cooled coil","Air cooled coil"]
["Fan","Quantity","","","","1","1","1","2","2","2","4"]
["","Type","","","","Axial","Axial","Axial","Axial","Axial","Axial","Axial"]
["Fan motor","Drive","","","","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive","Direct drive"]
["Compressor","Quantity","","","","1","2","2","3","4","4","6"]
["","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Operation range","Air side","Cooling","Min.","°CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Max.","°CDB","43","43","43","43","43","43","43"]
["","Water side","Evaporator","Min.","°CDB","-10 (4)","-10 (4)","-10 (4)","-10 (4)","-10 (4)","-10 (4)","-10 (4)"]
["","","","Max.","°CDB","20","20","20","20","20","20","20"]
["Sound power level","Cooling","","Nom.","dBA","78","78","78","80","81","81","83"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Circuits","","Quantity","","1","1","1","1","2","2","2"]
["Power supply","Phase","","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","0.0 (9)","77.7","78.7","88.7","99.8","101.9","120.7"]
["","Running current","","Max","A","22.2","25.3","26.4","35.2","47.4","49.6","67.2"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C"]
["","","","","","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(2) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(3) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti","(4) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL opti"]
["","","","","","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(5) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]
["","","","","","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)","(6) - Excluding the water volume in the unit. This volume will guarantee suficient defrost energy for all applications, however, this volume can be multiplied by 0,66 if the heating sepoint is ≥ 45° C (eg. Fan coils)"]
["","","","","","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(7) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop."]
["","","","","","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel","(8) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor","(9) - No peak current because of inverter compressor"]